## Instructions
Johnson Controls (Christchurch)
MX1CAL
SF0332 Version 1.2
MX1 System Design Calculation Tool
This tool has been prepared to assist MX1 system designers.
The "Loop Calculator" page allows you to validate your analogue loop design
The "Isolator Base Calculations" page allows you to check loop loadings between Isolator Bases
The "IS Spur Calculation" page allows you to check loop loadings from Intrinsically Safe devices
The "Aust Panel Calculator" page allows you to check overall system design parameters for an Australian application.
The "NZ Panel Calculator" page allows you to check overall system design parameters for a New Zealand application.
In general the procedure for using this tool is to:
1. | Fill in the details of your proposed system in the yellow cells
2. | Check and/or implement the resulting details in the blue cells
3. | Correct any problems that are indicated in red cells
System Name:
Designer:
Date:
Notes:
1. | Not all the devices listed in this calculator are approved in all situations. You need to check the current status before use.

## Loop Calculator
MX1 Loop Calculator
Loop 1 | go to Loop 2
| Fill in Yellow Cells. | Check Blue Cells |  |  | Any Red Cells indicate Problems
|  |  |  | Loop Currents | [5 empty] | Additional 24V Currents | [5 empty] | Cable data from RefData worksheet.
Device | Description | Number |  | DC mA | Alarm mA | AC Units | DC Total | Alarm Total | AC Total | Normal | Alarm | DC Total | Alarm Total | AZM800 Working for Alarm Allowance |  | Type |  |  | Cable size
814PH | Photo/heat Detector |  |  | 0.275 | 0.275 | 1 | 0 | 0 | 0 |  |  |  |  | 0 |  | Radox |  |  | 0.75
814P | Photo Detector |  |  | 0.275 | 0.275 | 1 | 0 | 0 | 0 |  |  |  |  | 0 |  | SWA |  |  | 1
814H | Heat Detector |  |  | 0.25 | 0.25 | 1 | 0 | 0 | 0 |  |  |  |  | 0 |  | TPS (screened) |  |  | 1.5
814CH | CO / Heat Detector |  |  | 0.275 | 0.275 | 1 | 0 | 0 | 0 |  |  |  |  | 0 |  | TPS (unscreened) |  |  | 2.5
814I | Ionisation Detector |  |  | 0.33 | 0.33 | 1 | 0 | 0 | 0 |  |  |  |  | 0 |  |  |  |  | 4
801PC | CO / Photo / Heat Detector |  |  | 0.3 | 0.3 | 2 | 0 | 0 | 0 |  |  |  |  | 0
801F | Flame Detector |  |  | 0.3 | 0.3 | 1 | 0 | 0 | 0 |  |  |  |  | 0
AZM800 | Apartment Zone Module - normal current |  |  | 4 | 4 | 1 | 0 | 0 | 0 |  |  |  |  | 0
| Apartment Zone Module - low current |  |  | 2.7 | 2.7 | 1 | 0 | 0 | 0 |  |  |  |  | 0 |  |  |  |  | Max Loop Current
| AZM with no conventional dets or MCPs |  |  | 3 | 3 | 1 | 0 | 0 | 0 |  |  |  |  | 0 |  |  |  |  | 1000
| Max. AZM800 detector circuits in alarm | 0 |  |  | 16 |  |  | 0
CP820 | Manual Call point (Australian) |  |  | 0.275 | 0.275 | 1 | 0 | 0 | 0 |  |  |  |  | 0
CIM800 | Contact Input Module |  |  | 0.275 | 0.275 | 1 | 0 | 0 | 0 |  |  |  |  | 0
DIM800 | Detector Interface Module |  |  | 0.28 | 0.28 | 1 | 0 | 0 | 0 | 14 | 50 | 0 | 0 | 0
| Detector quiescent current total (mA) | [10 empty] | 0 | 0 | 0
LPS800 | Loop Powered Sounder Driver Module |  |  | 0.45 | 0.45 | 1.5 | 0 | 0 | 0 |  |  |  |  | 0
| Total Alarm Load on all LPS800s (mA) | [6 empty] | 0 | [5 empty] | 0
| Total Non-alarm Load on all LPS800s (mA) | [5 empty] | 0 | [6 empty] | 0
| For each LPS800: greater of (4mA+Output Current) or 12mA | [12 empty] | 0
MIM800 | Monitored I/P Module (NO) |  |  | 0.275 | 0.275 | 1 | 0 | 0 | 0 |  |  |  |  | 0
MIM801 | Monitored I/P Module (NC) |  |  | 0.275 | 0.275 | 1 | 0 | 0 | 0 |  |  |  |  | 0
1841MX | Manual Call Point (NZ) |  |  | 0.275 | 0.275 | 1 | 0 | 0 | 0 |  |  |  |  | 0
MIO800 | Multiple Input Output Module |  |  | 0.48 | 0.48 | 1.2 | 0 | 0 | 0 |  |  |  |  | 0
RIM800 | Relay Interface Module |  |  | 0.285 | 0.285 | 1 | 0 | 0 | 0 |  |  |  |  | 0
SNM800 | Sounder Notification Module |  |  | 0.45 | 0.45 | 1 | 0 | 0 | 0 |  |  |  |  | 0
| SNM800 Alarm Load total (mA) | [11 empty] | 0 | 0
| SNM800 Non-Alarm Load total (mA) | [10 empty] | 0 |  | 0
SAB801 | Addressable Beacon/Sounder Driver |  |  | 0.25 | 3.25 | 1 | 0 | 0 | 0 |  |  |  |  | 0
SAM800 | Addressable Sounder Driver Module |  |  | 0.25 | 0.25 | 1 | 0 | 0 | 0 |  |  |  |  | 0
VLC800MX | Addressable VESDA LaserCompact |  |  | 0.3 | 0.3 | 2 | 0 | 0 | 0 | 225 | 245 | 0 | 0 | 0
S271f+ | Triple IR Flame Detector (flameproof) |  |  | 0.5 | 0.5 | 2 | 0 | 0 | 0 |  |  |  |  | 0
0
IS Devices * | Loop 1- Intrinsically Safe Spurs | 0 |  |  |  |  | 0 | 0 | 0 |  |  |  |  | 0
| Go to Isolator Base calculation | [12 empty] | 0
LIM800 | MX Isolator Module |  |  | 0.16 | 0.16 | 0.1 | 0 | 0 | 0 |  |  |  |  | 0
5BI | MX Isolator Base |  |  | 0.08 | 0.08 | 0.2 | 0 | 0 | 0 |  |  |  |  | 0
814IB | MX Isolator Base |  |  | 0.15 | 0.15 | 0.1 | 0 | 0 | 0 |  |  |  |  | 0
802SB | MX Sounder Base (Loud) - loop powered |  |  | 0.2 | 6.8 | 0.5 | 0 | 0 | 0 |  |  |  |  | 0
| MX Sounder Base (Quiet) - loop powered |  |  | 0.2 | 1.2 | 0.5 | 0 | 0 | 0 |  |  |  |  | 0
812SB | MX Sounder Base - loop powered |  |  | 0.2 | 21 | 0.5 | 0 | 0 | 0 |  |  |  |  | 0
901SB | MX Sounder Base (Loud) - ext. powered |  |  | 0.2 | 0.2 | 0.5 | 0 | 0 | 0 | 0 | 6.8 | 0 | 0 | 0
| MX Sounder Base (Quiet) - ext. powered |  |  | 0.2 | 0.2 | 0.5 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0
912SB | MX Sounder Base - ext. powered |  |  | 0.2 | 0.2 | 0.5 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0
814SB | MX Sounder Base (Loud) - loop powered |  |  | 0.4 | 15 | 2.4 | 0 | 0 | 0 |  |  |  |  | 0
| MX Sounder Base (Medium) - loop powered |  |  | 0.4 | 12 | 2.4 | 0 | 0 | 0 |  |  |  |  | 0
| MX Sounder Base (Quiet) - loop powered |  |  | 0.4 | 9 | 2.4 | 0 | 0 | 0 |  |  |  |  | 0
814RB | MX Relay Base |  |  | 0.05 | 0.05 | 0.3 | 0 | 0 | 0 |  |  |  |  | 0
| Loop 1 - Total Loop Addresses | 0 | Not more than than 250 |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0 | Alarm current without AZM800 alarm current
[14 empty] | 31 | Recommended max AZM800s in alarm
| Loop Cable length (m) |  | m. Must be less than 2000m. |  |  |  |  | Constants |  | Formulae
| Total Spur Cable length (m) (excl. IS spurs) |  | m
| Loop cable gauge (e.g. 0.75 sq.mm, etc.) | 1 | sq.mm
| Cable Type (select from list) | TPS (unscreened)
| Resistance of 1000m 1sq mm | 36 | ohm
| Capacitance of 1000m | 140 | nF
| Total Remote LED Load (mA) |  | Typically 7mA per Remote LED
| Other Load from loop (mA) |  | (Unusual to have any)
| Max LED Current (mA) | 30 | (Number of LEDs on is automatically limited to 10)
| Total AC Units Including Cable | 0 | Must be less than 450.
| Total DC Quiescent Load (mA) | 0 | Includes 2 * IB fault current
| Total Alarm Load (mA) | 0 | Must be less than 1000mA
| Loop Resistance including isolators | 0 | ohms
Note 1 | Minimum loop Voltage (All load at start or end) | 37 | Must be > 20V; also at least 2V higher than min operating V of LPS800 loads
Note 2 | Minimum loop Voltage (Typical load distribution) | 37 | Must be > 20V; also at least 2V higher than min operating V of LPS800 loads
| Battery Quiescent Load (mA) | 0 | Transfers to Panel Calculation pages
| Battery Alarm Load (mA) | 0 | Transfers to Panel Calculation pages
Loop 2 | go to Loop 1
| Fill in Yellow Cells. | Check Blue Cells |  |  | Any Red Cells indicate Problems
|  |  |  | Loop Currents | [5 empty] | Additional 24V Currents | [5 empty] | Cable data from RefData worksheet.
Device | Description | Number |  | DC mA | Alarm mA | AC Units | DC Total | Alarm Total | AC Total | Normal | Alarm | DC Total | Alarm Total | AZM800 Working for Alarm Allowance |  | Type | R | C | Cable size
814PH | Photo/heat Detector |  |  | 0.275 | 0.275 | 1 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 | 0 | 0 | 0.75
814P | Photo Detector |  |  | 0.275 | 0.275 | 1 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 | 0 | 0 | 1
814H | Heat Detector |  |  | 0.25 | 0.25 | 1 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 | 0 | 0 | 1.5
814CH | CO / Heat Detector |  |  | 0.275 | 0.275 | 1 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 | 0 | 0 | 2.5
814I | Ionisation Detector |  |  | 0.33 | 0.33 | 1 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 | 0 | 0 | 4
801PC | CO / Photo / Heat Detector |  |  | 0.3 | 0.3 | 2 | 0 | 0 | 0 |  |  |  |  | 0
801F | Flame Detector |  |  | 0.3 | 0.3 | 1 | 0 | 0 | 0 |  |  |  |  | 0
AZM800 | Apartment Zone Module - normal current |  |  | 4 | 4 | 1 | 0 | 0 | 0 |  |  |  |  | 0
| Apartment Zone Module - low current |  |  | 2.7 | 2.7 | 1 | 0 | 0 | 0 |  |  |  |  | 0 |  |  |  |  | Max Loop Current
| AZM with no conventional dets or MCPs |  |  | 3 | 3 | 1 | 0 | 0 | 0 |  |  |  |  | 0 |  |  |  |  | 1000
| Max. AZM800 detector circuits in alarm | 0 |  |  | 16 |  |  | 0
CP820 | Manual Call point (Australian) |  |  | 0.275 | 0.275 | 1 | 0 | 0 | 0 |  |  |  |  | 0
CIM800 | Contact Input Module |  |  | 0.275 | 0.275 | 1 | 0 | 0 | 0 |  |  |  |  | 0
DIM800 | Detector Interface Module |  |  | 0.28 | 0.28 | 1 | 0 | 0 | 0 | 14 | 50 | 0 | 0 | 0
| Detector quiescent current total (mA) | [10 empty] | 0 | 0 | 0
LPS800 | Loop Powered Sounder Driver Module |  |  | 0.45 | 0.45 | 1.5 | 0 | 0 | 0 |  |  |  |  | 0
| Total Alarm Load on all LPS800s (mA) | [6 empty] | 0 | [5 empty] | 0
| Total Non-alarm Load on all LPS800s (mA) | [5 empty] | 0 | [6 empty] | 0
| For each LPS800: greater of (4mA+Output Current) or 12mA | [12 empty] | 0
MIM800 | Monitored I/P Module (NO) |  |  | 0.275 | 0.275 | 1 | 0 | 0 | 0 |  |  |  |  | 0
MIM801 | Monitored I/P Module (NC) |  |  | 0.275 | 0.275 | 1 | 0 | 0 | 0 |  |  |  |  | 0
1841MX | Manual Call Point (NZ) |  |  | 0.275 | 0.275 | 1 | 0 | 0 | 0 |  |  |  |  | 0
MIO800 | Multiple Input Output Module |  |  | 0.48 | 0.48 | 1.2 | 0 | 0 | 0 |  |  |  |  | 0
RIM800 | Relay Interface Module |  |  | 0.285 | 0.285 | 1 | 0 | 0 | 0 |  |  |  |  | 0
SNM800 | Sounder Notification Module |  |  | 0.45 | 0.45 | 1 | 0 | 0 | 0 |  |  |  |  | 0
| SNM800 Alarm Load total (mA) | [11 empty] | 0 | 0
| SNM800 Non-Alarm Load total (mA) | [10 empty] | 0 |  | 0
SAB801 | Addressable Beacon/Sounder Driver |  |  | 0.25 | 3.25 | 1 | 0 | 0 | 0 |  |  |  |  | 0
SAM800 | Addressable Sounder Driver Module |  |  | 0.25 | 0.25 | 1 | 0 | 0 | 0 |  |  |  |  | 0
VLC800MX | Addressable VESDA LaserCompact |  |  | 0.3 | 0.3 | 2 | 0 | 0 | 0 | 225 | 245 | 0 | 0 | 0
S271f+ | Triple IR Flame Detector (flameproof) |  |  | 0.5 | 0.5 | 2 | 0 | 0 | 0 |  |  |  |  | 0
0
IS Devices * | Loop 2 - Intrinsically Safe Spurs | 0 |  |  |  |  | 0 | 0 | 0 |  |  |  |  | 0
| Go to Isolator Base calculation | [12 empty] | 0
LIM800 | MX Isolator Module |  |  | 0.16 | 0.16 | 0.1 | 0 | 0 | 0 |  |  |  |  | 0
5BI | MX Isolator Base |  |  | 0.08 | 0.08 | 0.2 | 0 | 0 | 0 |  |  |  |  | 0
814IB | MX Isolator Base |  |  | 0.15 | 0.15 | 0.1 | 0 | 0 | 0 |  |  |  |  | 0
802SB | MX Sounder Base (Loud) - loop powered |  |  | 0.2 | 6.8 | 0.5 | 0 | 0 | 0 |  |  |  |  | 0
| MX Sounder Base (Quiet) - loop powered |  |  | 0.2 | 1.2 | 0.5 | 0 | 0 | 0 |  |  |  |  | 0
812SB | MX Sounder Base - loop powered |  |  | 0.2 | 21 | 0.5 | 0 | 0 | 0 |  |  |  |  | 0
901SB | MX Sounder Base (Loud) - ext. powered |  |  | 0.2 | 0.2 | 0.5 | 0 | 0 | 0 | 0 | 6.8 | 0 | 0 | 0
| MX Sounder Base (Quiet) - ext. powered |  |  | 0.2 | 0.2 | 0.5 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0
912SB | MX Sounder Base - ext. powered |  |  | 0.2 | 0.2 | 0.5 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0
814SB | MX Sounder Base (Loud) - loop powered |  |  | 0.4 | 15 | 2.4 | 0 | 0 | 0 |  |  |  |  | 0
| MX Sounder Base (Medium) - loop powered |  |  | 0.4 | 12 | 2.4 | 0 | 0 | 0 |  |  |  |  | 0
| MX Sounder Base (Quiet) - loop powered |  |  | 0.4 | 9 | 2.4 | 0 | 0 | 0 |  |  |  |  | 0
814RB | MX Relay Base |  |  | 0.05 | 0.05 | 0.3 | 0 | 0 | 0 |  |  |  |  | 0
| Loop 2 - Total Loop Addresses | 0 | Not more than than 250 |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0 | Alarm current without AZM800 alarm current
[14 empty] | 31 | Recommended max AZM800s in alarm
| Loop Cable length (m) |  | m. Must be less than 2000m. |  |  |  |  | Constants |  | Formulae
| Total Spur Cable length (m) (excl. IS spurs) |  | m
| Loop cable gauge (e.g. 0.75 sq.mm, etc.) | 1 | sq.mm
| Cable Type (select from list) | TPS (unscreened)
| Resistance of 1000m 1sq mm | 36 | ohm
| Capacitance of 1000m | 140 | nF
| Total Remote LED Load (mA) |  | Typically 7mA per Remote LED
| Other Load from loop (mA) |  | (Unusual to have any)
| Max LED Current (mA) | 30 | (Number of LEDs on is automatically limited to 10)
| Total AC Units Including Cable | 0 | Must be less than 450.
| Total DC Quiescent Load (mA) | 0 | Includes 2 * IB fault current
| Total Alarm Load (mA) | 0 | Must be less than 1000mA
| Loop Resistance including isolators | 0 | ohms
Note 1 | Minimum loop Voltage (All load at start or end) | 37 | Must be > 20V; also at least 2V higher than min operating V of LPS800 loads
Note 2 | Minimum loop Voltage (Typical load distribution) | 37 | Must be > 20V; also at least 2V higher than min operating V of LPS800 loads
| Battery Quiescent Load (mA) | 0 | Transfers to Panel Calculation pages
| Battery Alarm Load (mA) | 0 | Transfers to Panel Calculation pages
Note 1 : Use this if the loop load is concentrated at one end of the loop, or if you are unsure.
Note 2 : Use this if the load is more or less uniformly distributed around the loop.
* These figures are calculated from the IS Spur Calculation sheet. All IS device quantities are recorded there.
Limits on the number of bases on at the same time
Limits on the number of bases on at the same time
Note on N20: Limit alarm current to 1 DIM only
Note on N94: Limit alarm current to 1 DIM only

## Isolator Base Calculations
MX1 Isolator Base Calculations
If Isolator Bases or LIM800 isolators are used, the number of devices between isolators is limited.
The following are examples of acceptable numbers of devices between 5BI or LIM800 isolators or AZM800.
Example 1 | 0-40 detectors + 0-10 Relay/Sounder Bases + 0-5 SNM800/RIM800 |  |  | Ancillary devices (MIM/CIM/DIM etc.) count
Example 2 | 0-40 detectors + 0-20 Relay/Sounder Bases |  |  | as a detector.
Example 3 | 0-40 detectors + 0-10 SNM800s/RIM800s
Example 4 | 0-60 detectors + 0-10 Relay/Sounder Bases
Fill in Yellow Cells.
There is no need to do specific IB calculations if using 5BI or LIM800 or AZM800 and your situation matches any of the above examples. | [7 empty] | Any Red Cells Indicate a Problem
If using 814IB Isolator Bases, then each section must be checked using the table below.
Any of your loop sections not covered by one or more of the above examples must be checked using the table below. | [8 empty] | Constants
Loop 1 | Back to Loop Calculation
go to Loop 2 | [5 empty] | Quantities
Device | Description | IB Units | Section 1 | Section 2 | Section 3 | Section 4 | Section 5 | Section 6 | Section 7 | Section 8 | Section 9 | Section 10
814PH | Photo/heat Detector | 1.2
814P | Photo Detector | 1.2
814H | Heat Detector | 1
814CH | CO / Heat Detector | 1
814I | Ionisation Detector | 1.4
801PC | CO / Photo / Heat Detector | 1
801F | Flame Detector | 7
AZM800 | Apartment Zone Module | 1.5
CP820 | Manual Call point (Australian) | 1.5
CIM800 | Contact Input Module | 1
DIM800 | Detector Interface Module | 1
LPS800 | Loop Powered Sounder Driver Module | 1
MIM800 | Monitored I/P Module (NO) | 1.5
MIM801 | Monitored I/P Module (NC) | 1.5
1841MX | Manual Call Point (NZ) | 1.5
MIO800 | Multiple Input Output Module | 3
RIM800 | Relay Interface Module | 5
SNM800 | Sounder Notification Module | 5
SAB801 | Addressable Beacon/Sounder Driver | 2.5
SAM800 | Addressable Sounder Driver Module | 1
VLC800MX | Addressable VESDA LaserCompact | 1
S271f+ | Triple IR Flame Detector (flameproof) | 2
802SB | MX Sounder Base (Loud) - loop powered | 2.5
| MX Sounder Base (Quiet) - loop powered | 2.5
812SB | MX Sounder Base - loop powered | 2.5
901SB | MX Sounder Base (Loud) - ext. powered | 2.5
| MX Sounder Base (Quiet) - ext. powered | 2.5
912SB | MX Sounder Base - ext. powered | 2.5
814SB | MX Sounder Base (Loud) - loop powered | 2.5
| MX Sounder Base (Medium) - loop powered | 2.5
| MX Sounder Base (Quiet) - loop powered | 2.5
814RB | MX Relay Base | 1.6
| IB Units in any section - |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- must be less than 100 for 5BI or LIM800 or AZM800
- must be less than 32 for 814IB
Loop 2 | Back to Loop Calculation
go to Loop 1 | [5 empty] | Quantities
Device | Description | IB Units | Section 1 | Section 2 | Section 3 | Section 4 | Section 5 | Section 6 | Section 7 | Section 8 | Section 9 | Section 10
814PH | Photo/heat Detector | 1.2
814P | Photo Detector | 1.2
814H | Heat Detector | 1
814CH | CO / Heat Detector | 1
814I | Ionisation Detector | 1.4
801PC | CO / Photo / Heat Detector | 1
801F | Flame Detector | 7
AZM800 | Apartment Zone Module | 1.5
CP820 | Manual Call point (Australian) | 1.5
CIM800 | Contact Input Module | 1
DIM800 | Detector Interface Module | 1
LPS800 | Loop Powered Sounder Driver Module | 1
MIM800 | Monitored I/P Module (NO) | 1.5
MIM801 | Monitored I/P Module (NC) | 1.5
1841MX | Manual Call Point (NZ) | 1.5
MIO800 | Multiple Input Output Module | 3
RIM800 | Relay Interface Module | 5
SNM800 | Sounder Notification Module | 5
SAB801 | Addressable Beacon/Sounder Driver | 2.5
SAM800 | Addressable Sounder Driver Module | 1
VLC800MX | Addressable VESDA LaserCompact | 1
S271f+ | Triple IR Flame Detector (flameproof) | 2
802SB | MX Sounder Base (Loud) - loop powered | 2.5
| MX Sounder Base (Quiet) - loop powered | 2.5
812SB | MX Sounder Base - loop powered | 2.5
901SB | MX Sounder Base (Loud) - ext. powered | 2.5
| MX Sounder Base (Quiet) - ext. powered | 2.5
912SB | MX Sounder Base - ext. powered | 2.5
814SB | MX Sounder Base (Loud) - loop powered | 2.5
| MX Sounder Base (Medium) - loop powered | 2.5
| MX Sounder Base (Quiet) - loop powered | 2.5
814RB | MX Relay Base | 1.6
| IB Units in any section - |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- must be less than 100 for 5BI or LIM800 or AZM800
- must be less than 32 for 814IB

## IS Spur Calculation
MX1 Intrinsically Safe Spur Calculations
Intrinsically Safe devices are connected to the MX Loop via an EXI800 interface and a galvanic isolator by Pepperl & Fuchs. | [13 empty] | IS Cable types from RefData worksheet. | [5 empty] | Gas group types from RefData sheet
The wiring in the hazardous area is a spur from the MX Loop. It can't be a loop in itself. It must be a single zone. | [13 empty] | Type | [5 empty] | IIA
There can be up to eight IS spurs on any one MX Loop. | [13 empty] | MICC 2H1 | [5 empty] | IIB
The IS isolators and devices present a heavy AC loading to the MX Loop, and the loading increases faster as more devices are added. | [13 empty] | MICC 2H1.5 | [5 empty] | IIC
This worksheet uses the method described in MX publication 17A-02-ISLOOP, issue 4, Plus FV421i data to calculate the MX loading effect. | [13 empty] | MICC 2L1
This worksheet uses the Gas Group cable limits from the ATEX certification for System 800 devices. | [13 empty] | MICC 2L1.5
The results of the IS Spur loading will need to be transferred to MX1Cost manually to calculate an overall MX Loop operation. | [13 empty] | Radox 1.0
SWA 1.5
Instructions | [13 empty] | SWA 2.5
For each IS spur being used, enter the numbers of devices in the yellow cells. | [13 empty] | TPS 1.0 (screened)
EXI800 and galvanic isolators are added automatically to any spur column with devices. | [6 empty] | Fill in Yellow Cells. | [6 empty] | TPS 1.0 (unscreened)
Select the type of cable and length being used for the spur. | [6 empty] | Any Red Cells Indicate a Problem
Select the required Gas Group rating for the spur. | [10 empty] | Constants |  | Formulae
For spurs that are not being used, ensure all yellow cells are blank.
Transfer the results to MX1Cost as per LT0441 Section 6.6 / LT0361 Section 7.6
Loop 1 | back to MX Loop Calculator | [17 empty] | IS Unit Breakpoint
go to Loop 2 |  |  |  |  | Quantities | [5 empty] | DC Unit totals | [7 empty] | 15 |  | IS Unit Totals (cumulative down a column)
Device | Description | Spur 1 | Spur 2 | Spur 3 | Spur 4 | Spur 5 | Spur 6 | Spur 7 | Spur 8 | DC Units | Spur 1 | Spur 2 | Spur 3 | Spur 4 | Spur 5 | Spur 6 | Spur 7 | Spur 8 | IS Units 1 | IS Units 2 | Spur 1 | Spur 2 | Spur 3 | Spur 4 | Spur 5 | Spur 6 | Spur 7 | Spur 8
EXI800 | IS Loop Interface (one per spur) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
P&F Isolator | Galvanic Isolator (one per spur) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6
801PHEx | Photo/Heat Detector | [8 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801CHEx | CO / Heat Detector | [8 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801HEx | Heat Detector | [8 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801FEx | Flame Detector | [8 empty] | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CP840Ex | Manual Call point | [8 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IF800Ex | Input Module | [8 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cable | Cable type (select from list) | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | nF cable capacitance
| Spur length (metres) | [17 empty] | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S271i+ | Flame Detector | [8 empty] | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FV421i | Flame Detector | [8 empty] | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Required Gas Group rating for spur | [8 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Results | DC Load from Loop (mA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Gas Group cable limiting values
| IS Units | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Cable capacitance of spur (nF) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Cable inductance of spur (mH) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Cable L/R ratio (uH/ohm) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Number of IS spurs | 0
| Maximum IS Units per spur | 0 | (depends on the number of spurs)
| Minimum IS Units per spur | 0 | (depends on the number of spurs)
| Total DC load of IS spurs | 0 | mA (transfers to loop calculation page)
| Total AC Load of IS spurs | 0 | AC Units (transfers to loop calculation page)
| Total device addresses | 0 | (transfers to loop calculation page)
IS Unit Breakpoint
Loop 2 | back to MX Loop Calculator | [9 empty] | DC Unit totals | [7 empty] | 15 |  | IS Unit Totals (cumulative down a column)
go to Loop 1 |  |  |  |  | Quantities |  |  |  |  | DC Units | Spur 1 | Spur 2 | Spur 3 | Spur 4 | Spur 5 | Spur 6 | Spur 7 | Spur 8 | IS Units 1 | IS Units 2 | Spur 1 | Spur 2 | Spur 3 | Spur 4 | Spur 5 | Spur 6 | Spur 7 | Spur 8
Device | Description | Spur 1 | Spur 2 | Spur 3 | Spur 4 | Spur 5 | Spur 6 | Spur 7 | Spur 8 | DC Units | Spur 1 | Spur 2 | Spur 3 | Spur 4 | Spur 5 | Spur 6 | Spur 7 | Spur 8 | IS Units 1 | IS Units 2 | Spur 1 | Spur 2 | Spur 3 | Spur 4 | Spur 5 | Spur 6 | Spur 7 | Spur 8
EXI800 | IS Loop Interface (one per spur) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
P&F Isolator | Galvanic Isolator (one per spur) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6
801PHEx | Photo/Heat Detector | [8 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801CHEx | CO / Heat Detector | [8 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801HEx | Heat Detector | [8 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801FEx | Flame Detector | [8 empty] | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CP840Ex | Manual Call point | [8 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IF800Ex | Input Module | [8 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cable | Cable type (select from list) | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | nF cable capacitance
| Spur length (metres) | [17 empty] | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S271i+ | Flame Detector | [8 empty] | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FV421i | Flame Detector | [8 empty] | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Required Gas Group rating for spur | [8 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Results | DC Load from Loop (mA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Gas Group cable limiting values
| IS Units | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Cable capacitance of spur (nF) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Cable inductance of spur (mH) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| Cable L/R ratio (uH/ohm) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Number of IS spurs | 0
| Maximum IS Units per spur | 0 | (depends on the number of spurs)
| Minimum IS Units per spur | 0 | (depends on the number of spurs)
| Total DC load of IS spurs | 0 | mA (transfers to loop calculation page)
| Total AC Load of IS spurs | 0 | AC Units (transfers to loop calculation page)
| Total device addresses | 0 | (transfers to loop calculation page)
Note on T31: IS units per 10nF
Note on K34: Richard Cree: Plus 3mA for first FV421i in alarm
Note on U36: Totals include the EXI800 and isolator IS loads
Note on T63: IS units per 10nF
Note on K66: Richard Cree: Plus 3mA for first FV421i in alarm
Note on U68: Totals include the EXI800 and isolator IS loads

## NZ Panel Calculator
MX1 NZ Panel Calculator
NO
Fill in Yellow Cells. |  |  |  |  | YES
Check Results in Blue Cells
Any Red Cells Indicate a Problem
| Qty | Quiescent Load (mA) | Alarm Load (including Quiescent) (mA)
MX Loop 1 (from Loop Calculator page) |  | 0 | 0 | mA
MX Loop 2 (from Loop Calculator page) |  | 0 | 0
Controller Board |  | 120 | 150 | mA
Display/Keyboard Module |  | 30 | 150 | mA
Zone LED Display Boards |  | 16 | 56 | mA
MX Loop Card |  | 50 | 50 | mA each
T-GEN 50 |  | 64 | 2200 | mA each
Mini-Gen (0-3) |  | 0 | 900 | mA each
Strobes |  | 0 | 100 | mA each
SGD (0 or 1) |  | 10 | 10 | mA each
Additional battery-backed Load (mA) |  |  |  | mA
Total battery loads |  | 166 | 356 | mA
Brigade Connected (select YES or NO) | YES
Door holders |  | 50 | 0 | mA each
Additional non-battery load (mA) |  |  |  | mA
Total non-battery loads |  | 0 | 0 | mA
Total quiescent (VB + VNB) | 166 | mA
Standby Time | 24 | hr
Alarm Time | 0.5 | hr
Standby discharge | 3.984 | Ah
Alarm discharge (20hr equivalent) | 0.356 | Ah
Minimum Battery Capacity (Ah) | 4.34 | Ah
Minimum PSU Rating (A) | 0.40506 | A (Must be less than 5A for standard PSU)
Constants
Formulae
Note on D11: Assumes 5 alarm indicators on
Note on D12: Device alarm load calculated separately
Note on D13: Fully loaded T-Gen
Note on D14: Fully loaded Mini-Gen
Note on C19: Non Alarm Load
Note on D19: Alarm Load

## Aust Panel Calculator
MX1 Australian Panel Calculator
Fill in Yellow Cells. |  |  |  |  | NO
Check Results in Blue Cells |  |  |  |  | YES
Any Red Cells Indicate a Problem
| Qty | Quiescent Load (mA) | Alarm Load (including Quiescent) (mA)
MX Loop 1 (from Loop Calculator page) |  | 0 | 0 | mA
MX Loop 2 (from Loop Calculator page) |  | 0 | 0
Controller Board |  | 120 | 150 | mA
Display/Keyboard Module |  | 30 | 150 | mA
Zone LED Display Boards |  | 16 | 56 | mA
MX Loop Card |  | 50 | 50 | mA each
T-GEN 50 |  | 64 | 2200 | mA each
Mini-Gen (0-3) |  | 0 | 900 | mA each
ASE (0 or 1) |  | 50 | 50 | mA each
Strobe Lights |  | 0 | 100 | mA each
Additional battery-backed load (mA) |  |  |  | mA
Total |  | 166 | 356 | mA
Brigade Connected (select YES or NO) | YES
Door holders |  | 50 | 0 | mA each
Additional non-battery load (mA) |  |  |  | mA
Total non-battery loads |  | 0 | 0 | mA
Total quiescent (VB + VNB) | 166 | mA
Standby Time | 24 | hr
Alarm Time | 0.5 | hr
Standby discharge | 3.984 | Ah
Alarm discharge (20hr equivalent) | 0.356 | Ah
24hr recharge requirement | 1.186 | Ah
Minimum Battery Capacity (Ah) | 5.425 | Ah
Minimum PSU Rating (A) | 0.42133 | A (Must be less than 5A for standard PSU)
Constants
Formulae
Note on D11: Assumes 5 alarm indicators on
Note on D13: Fully loaded T-Gen
Note on D14: Fully loaded Mini-Gen
Note on C19: Non Alarm Load
Note on D19: Alarm Load

## RefData (hidden)
Reference Data for Calculations
These numbers are used in the calculations on the other sheets.
To improve the clarity and maintenance of this spreadsheet, these numbers
are defined here and referenced by name, with some explanation, where this may help.
This sheet is normally protected. Do not alter numbers on this sheet
unless you understand what you are doing.
General
Battery charging efficiency | 80%
MX Loop O/C Voltage | 37 | V, at the loop terminals with no load
Loop Isolator fault current | 7 | mA (2 x 3.5mA)
Loop Isolator resistance (LIM800, 5BI) | 0.25 | ohm
Loop Isolator resistance (DDM800, AZM800) | 0.1 | ohm
Base LED Current | 3 | mA (internal LEDs)
MX Loop to battery current factor | 2 | Reflects the conversion ratio of the +V to 40V converter in MX1
Heavy load battery factor | 2 | Converts heavier battery discharges to an effective C20 load. Termed "Fc" in AS1670.1.
New Zealand factors
Connected standby time | 24 | hours
Local standby time | 72 | hours
Alarm time | 0.5 | hours
Connection test interval | 30 | seconds
Connection test duration | 400 | milliseconds
Effective charger duty cycle | 98.67% | on a minute by minute basis
Long term test interval | 24 | hours
Long term test duration | 60 | minutes
Effective 24 hour charger availability | 94.56% | on a daily basis
Australian factors
Connected standby time | 24 | hours
Local standby time | 72 | hours
Alarm time | 0.5 | hours
Recharge standby time | 5 | hours (after 24 hours recharge of battery)
Connection test interval | 30 | seconds
Connection test duration | 400 | milliseconds
Effective charger duty cycle | 98.67% | on a minute by minute basis
Long term test interval | 24 | hours
Long term test duration | 60 | minutes
Effective 24 hour charger availability | 94.56% | on a daily basis
Battery age derating factor | 1.25 | (oversize factor for new battery to allow for capacity loss from aging)
MX Loop factors
Max loop length | 2000 | m
AC Units | 2 | nF per unit
Max AC Units | 450 | per loop
DC Units | 0.25 | mA per unit
Max DC Load | 1000 | mA per loop
Worst case loading factor | 100% | all load at beginning or end of loop
Typical loading factor | 75% | load is more spread out around loop
Max remote LEDs on | 10 | MX1 limits the number of remote LEDs driven by detectors to this number
Cable Data | R | C
Radox | 47 | 200 | Units are loop ohm/km per 1 sq.mm, and nF/km
SWA | 36 | 580
TPS (screened) | 36 | 375
TPS (unscreened) | 36 | 140
IS Cable data | R | C | L | L/R
MICC 2H1 | 36 | 400 | 0.83 | 27 | Units are loop ohm/km, nF/km, uH/km, uH/ohm
MICC 2H1.5 | 24 | 400 | 0.42 | 37 | Must be in ascending order in first column (cable type)
MICC 2L1 | 36 | 600 | 0.66 | 21 | Update secondary table ranges on other worksheets for changes
MICC 2L1.5 | 24 | 600 | 0.63 | 30
Radox 1.0 | 47 | 200 | 0.65 | 9
SWA 1.5 | 24 | 560 | 0.33 | 28
SWA 2.5 | 14.5 | 600 | 0.32 | 45
TPS 1.0 (screened) | 36 | 375 | 0.65 | 9.3
TPS 1.0 (unscreened) | 36 | 140 | 0.65 | 9.3
IS Loading Calculation data | No. of Spurs | Max IS/spur | Min IS/spur | Unused IS to AC factor
| 1 | 74 | 0 | 5.6
| 2 | 62 | 0 | 3.6
| 3 | 39 | 0 | 3
| 4 | 37 | 0 | 2.5
| 5 | 30 | 16 | 2.1
| 6 | 26 | 16 | 1.7
| 7 | 23 | 16 | 1.4
| 8 | 20 | 16 | 1.2
IS cable unit | 10 | nF
| CP840Ex, IF800Ex only |  |  | Other detector types
IS Gas Group cable limit data | C | L | L/R | C | L | L/R
IIA | 2150 | 126 | 479 | 2140 | 35 | 444
IIB | 650 | 59 | 241 | 640 | 17 | 210
IIC | 83 | 15.8 | 65 | 77 | 4.3 | 56

## ChangeLog (hidden)
SF0332 MX1CAL - Change Log
Version | Date | Ref | Change
1.00 | 2004-12-23 |  | Original
1.01 | 2005-01-21
1.02 | 2006-08-11 | ECO 3768 | Aust Panel page, RefData sheets added. New devices added to Loop Calculator. IS Calculation sheet added.
1.03 | 2008-12-08 | ECO 3947 | Added AZM800, SAB801, hyperlinks.
1.10 | 2009-04-16 | ECO 4017 | Added Loop 2 tables in Loop Calculator, Isolator Base, IS Spur sheets. Corrected error in Aus battery calculation. Added more hyperlinks for new tables. Added Gas Group limit check in IS Spur sheet.
1.2 | 2019-03-11 | ECO 5207 | Add FV421i to IS Spur Calculation